## Cross Conn Documentation
System Name
pwsid | [7 empty] | Page __ of __
CROSS CONNECTION CONTROL INVENTORY |  |  |  |  | Year
| Risk Assesment |  |  |  |  | Inspection
Device Location | Hazard | Continuous Pressure | Back Pressure | CCC Device Selected | ASSE Code | Testable | Test Date | Inspected | Initials
Links to additional information on cross connection control :
EPA Cross Connection Control Manuual
AWWA M14 Backflow Prevention and Cross-Connection Control
System Name
pwsid | [7 empty] | Page __ of __
CROSS CONNECTION CONTROL INVENTORY |  |  |  |  | Year
| Risk Assesement |  |  |  |  | Inspection
Location | Hazard | Continuous Pressure | Back Pressure | CCC Device Selected | ASSE Code | Testable | Test Date | Inspected | Initials
System Name
pwsid | [7 empty] | Page __ of __
CROSS CONNECTION CONTROL INVENTORY |  |  |  |  | Year
| Risk Assesement |  |  |  |  | Inspection
Location | Hazard | Continuous Pressure | Back Pressure | CCC Device Selected | ASSE Code | Testable | Test Date | Inspected | Initials
System Name
pwsid | [7 empty] | Page __ of __
CROSS CONNECTION CONTROL INVENTORY |  |  |  |  | Year
| Risk Assesement |  |  |  |  | Inspection
Location | Hazard | Continuous Pressure | Back Pressure | CCC Device Selected | ASSE Code | Testable | Test Date | Inspected | Initials
System Name
pwsid | [7 empty] | Page __ of __
CROSS CONNECTION CONTROL INVENTORY |  |  |  |  | Year
| Risk Assesement |  |  |  |  | Inspection
Location | Hazard | Continuous Pressure | Back Pressure | CCC Device Selected | ASSE Code | Testable | Test Date | Inspected | Initials
Implementing a Cross Connection Control Plan for Small Public Waterworks Systems
The sheet to the left , or a similar one, can be used to set up a systems cross connection control inventory for TNC, NTNC and small Community Waterworks.
As an initial risk assesement the grey areas can be utilized to determin risk and select the appropriate device.
See Sheets 2 for definition of risk asesemnt terms. See Sheet 3 to asist in the selection of the proper cross connection device. Cross connections are located via inspection of owner controlled plumbing. Community waterworks will also have to conduct inspections of commercial buildings and surveys of residential connections as part of the initital assesement.
As an annual inspection the completed inventory sheet can be printed out and the yellow sections filled in as items are verified. Document annual testing of any testable devices using the Test Report on Sheet 4. Completed annual inspection sheets and test reports must be maintained for a period of 10 years.
Community waterworks should also send out annual surveys to their concumers to see if any potential cross connections have been addded to the system. A sample surveys are located on Sheets 5 and 6. Sending these surveys out with the Consumer Confidence Report is a good way to document distribution. Returned surveys are used to update the inventory sheet and must be retained for a period of ten (10) years.
Additional information on implementing a cross connection control program can by downloading the following documents:

## Sheet 3 (Devise Matrix)
Cross Conneciton Device Selection Matrix
Approved for..
Device | Acronym | ASSE Code | Testable | High Hazard | Continuous Pressure | Back pressure (1)
Hose bib vacuum breaker | HBVB | 1011 | N | N | N | N
Air Gap | na | NA | N (6) | Y | na | na
Anti-siphon Ballcock | ASB | 1002 | N | Y | N | N
Flushometer | na | 1037 | N | Y | N | N
Salon basin vacuum breaker | na | 1014 | N | N | N | N
Atmospheric vacuum breaker | AVB | 1001 | N | Y | N | N
Pressure vacuum breaker | PVB | 1020 | Y | Y | Y | N
Double check with atmospheric vent | DCAV | 1012 | N | N | Y | Y
Double check with atmospheric vent | DCAV | 1035 | N | N | See Note (2) | Y
Double check with atmospheric vent (3) | DCAV | 1032 | N | N | Y | Y
Reduced Pressure zone backflow assembly | RPZ | 1013 | Y | Y | Y | Y
Double check valve assembly | DCVA | 1015 | Y | N | Y | N
Double check detector valve assembly | DCDVA | 1048 | Y | N | Y | N
Dual check valve (4) | DCV | 1024 | N | N | Y | Y
Notes:
1. Devices approved for continuous pressure and back pressure MUST provide for downstream thermal expansion.
2. Approval for use under continuous pressure conditions varies with manufacturer.
3. Typically used with soda fountain carbonators.
4. Approved for residential use only.
5. Installed testable devices MUST be tested annually. Devices failing annual tests must be repaired or replaced in a timely fashion.
6. Air gaps are not testable but they are inspectable. The minimum air gap must be 1.5 times the outlet pipe diameter above the flood rim of the recieving basin.

## Sheet 4 Sample Test Report
This form was downloaded from the EPA Cross Connection Control Manual
The maunal can be downloaded in full at:
http://www.epa.gov/safewater/pdfs/crossconnection/crossconnection.pdf

## Sheet 5 Commercial Survey Form
This form was downloaded from the EPA Cross Connection Control Manual

## Sheet 6 Residential Surve Form
System's may wish to develop a cross connection pamphlet
Link to example Residential Cross Connection Guidanance
http://whitinsvillewater.com/wp-content/uploads/2012/07/WWC-Cross-Connection-Brochure.pdf
System Name
Public Utilities requiers customers to inspect their residential plumbing to ensure that any cross connections are identified and are properly isolated from the public water supply.
Please see the attached brouchure or visit our web site. For additional infomation please contact ________________________________ at _________________________